## Slide 1
Protection of Microgrid Systems with High Penetration of Inverter-Based Resources
Max Ferrari and Leon Tolbert
CURENT Student Seminar
February 23, 2024

## Slide 2: Microgrid Protection: Scope and Contributions
Problem
Objectives
Answer the long-standing question if an IBR can be modified to provide high fault current during faults
Contributions
VSC designed to to provide 3.0. p.u. during faults
Protecting inverter-based microgrids is challenging because of small fault contribution of Inverter Based Resources (IBRs)
Fuse to relay and relay-to-relay coordination in a radial microgrid
Control method to maintain stability and bandwidth criteria during both normal and faults conditions
>20 years of research on microgrid protection has not led to a commercially available microgrid relay to date [4]
This research proposes hardware and control modifications to an energy storage system (battery and inverter) as a solution to the challenges of microgrid protection
Short-circuit current magnitude drastically changes depending on operation mode
Explore adaptive protection to provide a solution to microgrid protection
Model-adaptive relay to adjust the relay curves’ sensitivity depending on microgrid generation and mode of operation
Existing protective devices for distribution not suitable for microgrids
Notes:   Protecting inverter-based microgrids is challenging because of very small fault contribution of Inverter Based Resources (IBRs), typically 1.0 to 1.5 p.u [7-10].
  The short-circuit current magnitude in a microgrid drastically changes between grid-tied and islanded operation (50 p.u to 1.5 p.u) [4,6]
  Protective devices for distribution, such as reclosers, relays and fuses, are typically not suitable for microgrid protection due to the dependence of these devices on the magnitude of the fault current [27, 28, 31]
    Fuses are particularly affected because of their inverse characteristics; in some cases, fuses protecting the laterals will not melt for faults during islanded operation [11]
    Coordination between fuses and relays is typically unattainable in inverter based microgrids
  For complex microgrid with multiple DERs, may be multiple paths and bidirectional flow for the short-cirtcuit current
  Variable short circuit current due to intermittent generation
  >20 years of research on microgrid protection has not led to a commercially available microgrid relay to date [4]

## Slide 3: MICROGRID PROTECTION CHALLENGES: CASE STUDY
(a) EPB’s Riverside Microgrid. Green dashed line encloses the microgrid. (b) Time Current Curve (TCC) for 100A S&C Positrol fuse and Intellirupter (PCR 03778).
100 T Grid-Tied
(PV-Inverter Current Controlled)
3-phase Fault (.2 s)
40 times nominal
100 T Islanded
(PV-Inverter Voltage Controlled)
3-phase Fault (.2 s)
2 times nominal
(1)
Grid tied
Island
Grid-tied
Sunny day 2800 ARMS
off-grid
Sunny day 144ARMS
Load 25
293 kW 410 kva
(a)
(b)
Notes: Melt curve fuse

## Slide 4: COMMERCIAL PV INVERTER FAULT CHARACTERISTICS
Fault contribution for several PV inverter manufacturers
Transient for 33 kW, 3-ph PV inverter at rated power and unity power factor [47-51]. Fault current = Nominal current
Fault current limited to ~1.0 p.u.
PV inverters limit to ~ 1.0 p.u.
Brand | Model | Power Rating (kW) | Voltage rating (V) | Nominal Current (A) | Fault Current (A) | Ratio of Fault to Nominal
ABB | PRO-33.0-TL-OUTD | 33 | 480 | 50.3 | 50.3 | 1
ABB | TRIO-27.6-TL-OUTD | 28 | 480 | 45 | 46 | 1.02
FIMER | PVS-60-TL | 62 | 480 | 80 | 92 | 1.15
SMA | STP 30000TL-US-10 | 30 | 480 | 36.2 | 36.2 | 1.00
SMA | STP 50-US-40 | 50 | 480 | 60.2 | 64 | 1.06
SMA | STP 12000TL-20 | 12 | 280 | 17.4 | 17.4 | 1.00

## Slide 5: COMMERCIAL INVERTER FAULT CHARACTERISTICS
Fault current from leading energy storage inverter manufacturers
transient for 24 kW, 3-ph ES inverter at rated power and unity power factor [47-51].
Fault current limited to 1.5 p.u. current clipped
PV inverters limit to ~ 1.5 p.u.
Brand | Model | Power (kW) | Voltage (V) | Nominal Current (A) | Fault Current (A) | Ratio
Oztek | OZpcs-RS40 | 40 | 480 | 50 | 63 | 1.3
Dynapower | Micro Power System | 125 | 480 | 150 | 213 | 1.4
SMA | Sunny Boy Storage 2.5 | 2.5 | 280 | 10.5 | 19 | 1.8
Firmer | React2-uno-5.0-tl | 5.0 | 280 | 22 | 22 | 1.0

## Slide 6: CONVENTIONAL PROTECTION APPLIED TO MICROGRIDS 1
Overcurrent protection is advantageous as it is simple, cheap and allows coordination and the use of fuses to protect laterals. However, overcurrent protection is unattainable as the IBRs limit their short-circuit current to close to their nominal current

## Slide 7: CONVENTIONAL PROTECTION APPLIED TO MICROGRIDS 2
The problems of low short circuit current created the need to start using protective devices that are not dependent solely on the current magnitude

## Slide 8: CONVENTIONAL PROTECTION APPLIED TO MICROGRIDS 3
The problems of low short circuit current created the need to start using protective devices that are not dependent solely on the current magnitude

## Slide 9: PROTECTION OF MICROGRIDS IN THE U.S.
REFERENCES: 22,23,24.
Voltage/frequency
Differential
Overcurrent
Adaptive overcurrent
Synchronous Generation

## Slide 10: SUMMARY OF MICROGRID PROTECTION
Limited short-circuit current contribution from inverter-based generation causes many of the challenges when protecting microgrids in islanded operation.
Most previous work focus on the protective device for solutions instead of the culprit of the challenges, the inverter.
Line differential protection most effective way to protect microgrids. Drawbacks:
  very cost-prohibitive solution.
  requires a high bandwidth communication
  relay installation at every node of a protection zone,
  equipped with backup relays, such as directional overcurrent relays
Adaptive relay requires communication infrastructure and it may not be able to detect fault conditions if load is close to pickup.
  It does not solve fuse challenges.
  Limited to 4-7 protection settings groups
Other methods propose oversizing the whole IBR unit, which is cost prohibitive and impractical for real world applications.

## Slide 11
    VOLTAGE SOURCE CONVERTER (VSC) DESIGN WITH INCREASED SHORT-CIRCUIT CONTRIBUTION

## Slide 12
-Increase SCC of a generic VSC to enable legacy distribution protection
-Demonstrate full overcurrent coordination with fuses and reclosers
-Determine max SCC of normally rated IGBT
-Identify what components must be overrated to increase >3X SCC
-Evaluate full overcurrent coordination with fuses, primary relay and backup relay
-Evaluate LG,LL and 3-ph faults
-Grid-Filter inductor saturates at currents higher than its rated
-Nonlinear inductance introduces instabilities in the control
-Propose control to maintain stability criteria for normal and fault conditions
Objective
Control Approach
Coordination Study
Hardware Approach

## Slide 13: ADVANTAGES OF PROPOSED METHOD
1) Enables the utilization of affordable overcurrent devices such as fuses, circuit breakers and reclosers
2) Enables fuse-relay coordination, and coordination between primary and backup relays
3) It is cost-effective since only the semiconductor and current sensor are oversized, while the rest of the inverter components remain at the designed rated power
4) No dedicated or additional unit is required; the ESS or PV inverter can be modified to provide the higher fault current

## Slide 14: VSC DESIGN WITH INCREASED SHORT CIRCUIT CURENT CAPABILITY
Energy storage system (Battery) with two-level three-phase inverter
Overrated CT
Rated/Overrated same SDIP-25 package
Decoupling considering saturable inductors
Adaptive control based on available inductance

## Slide 15: ELECTROTHERMAL SIMULATION
Temperature
Electrothermal simulation block diagram

## Slide 16
Experimental results showing inverter current during three-phase faults. Rated device providing the following fault current: (a) 1.25 p.u, (b) 1.5 p.u, (c), (d) 2.0 p.u (d) 3.0 p.u. Overrated device providing the following fault current: (e) 2.5 p.u. (f) 3.0 p.u.
Simulated temperature response using 4-layer Foster network for the following cases: Rated device providing the following fault current: (a) 1.25 p.u, (b) 1.5 p.u, (c), (d) 2.0 p.u (d) 3.0 p.u. Overrated device providing the following fault current: (e) 2.5 p.u. (f) 3.0 p.u.
EXPERIMENTAL RESULTS, RATED VS OVERRATED MODULE UNDER 3-PH FAULTS
RATED DEVICE
OVERRATED

## Slide 17
IMPACTS OF OVERRATING POWER ELECTRONICS MODULE
ADDITIONAL BENEFITS OF OVERRATING POWER MODULE
Increases efficiency during normal operation (1.0 p.u.)
Enhanced grid support capabilities (LVRT, voltage support, frequency support)
Increased inertial response (more current available during transients)
Power losses prototype inverter (used in the research) and higher power inverter. Overrated device is more efficient at normal operation and provides high current capability
Normal Operation
Overrated Device Lower Losses & Junction Temp
PROTOTYPE INVERTER: (30A, 600V)
FULL SCALE INVERTER: (150A, 1200V)

## Slide 18: INDUCTOR SATURATION
Experimental characteristic of the nonlinear inductor used in this work. Inductor characterized at room temperature using DPG10 Power Choke Tester.
(2) Ferrite core (10A) HF applications (lower losses)
core saturates at lower flux density.
(1) Silicon Steel core (10A) Heavy and bulky
Typically found at LF applications
(3) Ferrite core (5A (4 x 334uH) HF applications (lower losses)
core saturates at lower flux density.

## Slide 19: CONTROL STABILITY WITH SATURABLE INDUCTORS
Bode plot for different inductance values due to core saturation effect of the steel iron core. L = 1.0 p.u. =1.2 mH. Controller gains (Kp = 0.75, Ki = 8.3)
Open Loop Transfer Function
PI
Time Delay
CC TF
Sensor Gain
-Stability margins depend on current setpoint.
-Severe oscillations when inductor saturates.
-Closed-loop current control may become unstable for deep core saturation.

## Slide 20: CONTROL INSTABILITY WHEN NOT CONSIDERING INDUCTOR SATURATION
Step response for different inductance values due to core saturation effect of the ferrite core.
Experimental results ferrite core closed loop control. Inverter becomes unstable for currents >25A.
I=10A, L=1 p.u.
I=25A, L=.7 p.u.
I=40A, L=.4 p.u.

## Slide 21: SECOND ORDER POLYNOMIAL VALIDATION
Ferrite core model validation with second order polynomial fit. (a) linear region (b) nonlinear region
(a)
(b)
Ferrite core (10A)
Second-order fit provided good representation of the nonlinearities of the inductor

## Slide 22: MODEL VALIDATION 3-PHASE INVERTER
(a) Simulation considering grid-filter saturation (b) experimental results
(a)
(b)
Second-order fit provided good representation of the nonlinearities of the inductor

## Slide 23: CONTROLLER DESIGN CONSIDERING NONLINEAR INDUCTOR IN THE DQ REFERENCE FRAME
Current transfer function
(1.7)
(1.8)
Small signal model of the inverter in dq coordinates including decoupling terms considering saturable inductors.
where

## Slide 24: PI CURRENT CONTROLLER DESIGN CONSIDERING CORE SATURATION
Problem: Constant PI Controller tuned considering linear inductor makes the control unstable during faults due to the core saturation.
Proposed Solution: Consider the core saturation in the calculation to adaptively adjust the controller gains. With this method, we can make the inverter stable during short-circuit faults.
The proposed method consists of adaptively adjusting the integral and proportional gains considering the operating point of the inverter.
Notes: he Butterworth polynomial is used to select the appropriate controller parameters
Butterworth polynomial and D-decomposition methods are applied to determine these parameters to ensure the system stability.

## Slide 25: PI CURRENT CONTROLLER DESIGN CONSIDERING CORE SATURATION
The Butterworth method locates the eigenvalues uniformly in the left-half s-plane on a circle with radius
(1.9)
Third-order Butterworth Polynomial optimizes the closed-loop eigenvalues
The closed loop transfer function for the current control:
.
Where the inductances are defined as:
(1.10)

## Slide 26: PROPOSED CONTROL
Comparing the coefficients in the Butterworth polynomial with the denominator of the closed-loop transfer function, we obtain:
Adaptive controller gains considering core saturation.
(1.11)
(1.12)
Normal Operation
Fault Operation

## Slide 27: PROPOSED CONTROL
PROPOSED METHOD
CONSTANT PI METHOD
Constant gain PI step response for different inductance values due to core saturation effect of the ferrite core . L = 1.0 p.u = 1.3 mH.
Bode plot for different inductance values due to core saturation effect of the ferrite core. L = 1.0 p.u = 1.3 mH. PI gains calculated using the Butterworth polynomial.
Same PM and GM margin regardless of the operating point
PM and GM margin depend on operating point

## Slide 28: EXPERIMENTAL RESULTS: CONSTANT PI vs. PROPOSED CONTROL CLOSED LOOP CONTROL. 3-PHASE FAULT.
Experimental results. 3-phase faults. Proposed adaptive method
Experimental results. 3-phase faults. PI constant gains.

## Slide 29: EXPERIMENTAL RESULTS: CONSTANT PI vs. PROPOSED CONTROL CLOSED LOOP CONTROL. LINE-LINE FAULT
Experimental results. LL faults. Proposed adaptive method
Experimental results. LL faults. PI constant gains.

## Slide 30: EXPERIMENTAL RESULTS: CONSTANT PI VS PROPOSED CONTROL CLOSED LOOP CONTROL. LINE-GROUND FAULTS.
Experimental results. LG faults. Proposed adaptive method
Experimental results. LG faults PI constant gains.

## Slide 31: COORDINATION STUDY
TCCs for the 12.5A fuse. SEL 651R used as primary and backup relay. The CTs for both relays are 50-1 ratio. The pickup for the primary relay is 0.46 with a time dial of 1.5. The backup relay has a pickup of 0.5 with a time dial of 2.5. U5 curve for 51 protections is used for primary and backup relay.
Coordination study includes:
Fuse-blow
Primary protection
Backup Protection
For 3ph, LL and LG faults
Fault current

## Slide 32: COORDINATION STUDY: FUSES
Fuse clearing times for (a) LG, (b) LL, (c) 3-ph faults. Experimental results read from SEL 651 (128 samples).
(a)
(b)
(c)

## Slide 33: COORDINATION STUDY: PRIMARY RELAY
Primary relay clearing times for (a) LG, (b) LL, (c) 3-ph faults. Experimental results read from SEL 651 (128 samples).
(a)
(b)
(c)

## Slide 34: COORDINATION STUDY: BACKUP RELAY
Backup relay clearing times for (a) LG, (b) LL, (c) 3-ph faults. Experimental results read from SEL 651 (128 samples).
(a)
(b)
(c)

## Slide 35: VSC DESIGN CONCLUSIONS
Demonstrated that by over-rating just a few components, inverter can provide more than 3.0 p.u. of short-circuit current.
3.0 p.u. proved to be the minimum current that allows protection coordination
An online method to calculate the proportional and integral gains based on the available grid-filter inductance was derived and validated in hardware.
Experimental testing showed that full coordination in an islanded system can be achieved for LG,LL and 3-ph faults.

## Slide 36: Publications
Maximilliano Ferrari, “Protection of Grid-Tied and Islanded Systems with High Penetration of Inverter-Based Resources” Ph.D. Dissertation, Energy Science and Engineering, The University of Tennessee, May 2023
M. Ferrari, L. M. Tolbert, “Inverter Design with High Short-Circuit Fault Current Contribution to Enable Legacy Overcurrent Protection for Islanded Microgrids,” IEEE Power and Energy Society General Meeting, Denver, CO, July 17-21, 2022, pp. 1-5
M. Ferrari, L. M. Tolbert, “Grid-tied PV Inverter With Oversized Power Module To Increase Its Low-voltage Ride Through (LVRT) Capabilities and VAR Support,” IEEE PES Innovative Smart Grid Technologies Latin America, San Juan, Puerto Rico, Nov. 6-9, 2023
A. Sundararajan, M. Olama, M. Ferrari, B. Ollis and G. Liu, "A Data Quality-Aware Framework to Reliably Forecast Photovoltaic Generation and Consumer Load for an Improved Resilience of Microgrids," 2022 IEEE 13th International Symposium on Power Electronics for Distributed Generation Systems (PEDG), 2022, pp. 1-6, doi: 10.1109/PEDG54999.2022.9923109.
M. Ferrari, B. Park and M. M. Olama, "Design and Evaluation of a Model-Free Frequency Control Strategy in Islanded Microgrids with Power-Hardware-in-the-Loop Testing," 2021 IEEE Power & Energy Society Innovative Smart Grid Technologies Conference (ISGT), 2021, pp. 1-5, doi: 10.1109/ISGT49243.2021.9372219.
Piesciorovsky, EC, Ferrari Maglia, MF. Comparison of high-speed adaptive and nonadaptive backup overcurrent protection on fuse feeders with sensors. Int Trans Electr Energ Syst. 2019; 29:e2812.